## Sheet1
Load Calculation for Auditorium
Distribution Board
SL no | Descripting of Items | Considered Rating(Watt) | Quantity | Total Wattage | D.F(%) | Maximum Demand(Watt)
i. | Lights
| Circular LED Light | 60 | 30 | 1800 | 60% | 1080
| Flat LED Light | 80 | 2 | 160 | 60% | 96
| Wall bracket light (WL) | 40 | 5 | 200 | 60% | 120
| Ceiling light (CL) | 40 | 2 | 80 | 60% | 48
| 13A -3pin (type-S) | 1000 | 5 | 5000 | 60% | 3000
| Wall Mounted Speaker | 600 | 5 | 3000 | 100% | 3000
Total Maximum Demand(Including SDB1+SDB2+SDB3) | [5 empty] | 64314.1
|  |  |  | with 10% spare |  | 70745.51
|  | Therefore, I |  |  |  | 123.0269
|  |  |  | with25% of RF |  | 153.7837
Circuit Breaker : 160A TP MCCB
Cable: 4x1C-50mm2 NYY + 1x1c-16mm2 BYA as ECC
Sub Distribution Board-01
Serial No | Descripting of Items | Considered Rating(Watt) | Quantity | Total Wattage | D.F(%) | Maximum Demand(Watt)
i. | AC Loads
| Central AC | 3000 | 11 | 33000 | 100% | 33000
0
Total Maximum Demand | [5 empty] | 33000
|  |  |  | with 10% spare |  | 36300
|  | Therefore, I |  |  |  | 63.1259
|  |  |  | with25% of RF |  | 78.9074
Circuit Breaker : 80A DP MCB
Cable: 4x1C-25mm2 NYY + 1x1c-16mm2 BYA as ECC
Sub Distribution Board-02
Serial No | Descripting of Items | Considered Rating(Watt) | Quantity | Total Wattage | D.F(%) | Maximum Demand(Watt)
i. | Lights
| Flat LED Light | 80 | 4 | 320 | 60% | 192
| Mirror Light | 15 | 4 | 60 | 60% | 36
| Tube Light | 40 | 5 | 200 | 60% | 120
| Wall bracket light (WL) | 40 | 16 | 640 | 60% | 384
| Stage Spot Light | 800 | 3 | 2400 | 60% | 1440
| Incandascent Rotating Stage Lights | 1500 | 3 | 4500 | 60% | 2700
| Ceiling light (CL) | 40 | 8 | 320 | 60% | 192
ii. | Fan
| Ceiling Fan | 75 | 3 | 225 | 50% | 112.5
| Wall Mounted Fan | 45 | 2 | 90 | 50% | 45
ii. | Power Sockets
| 5A-2pin | 300 | 6 | 1800 | 50% | 900
| 13A-3pin | 1000 | 5 | 5000 | 60% | 3000
iii. | AC Loads
| AC(1.5 TON) | 1500 | 2 | 3000 | 100% | 3000
iv. | Others
| Washroom Exhaust Fan | 36 | 4 | 144 | 60% | 86.4
Total Maximum Demand | [5 empty] | 12207.9
|  |  |  | with 10% spare |  | 13428.69
|  | Therefore, I |  |  |  | 23.3526
|  |  |  | with25% of RF |  | 29.1907
Circuit Breaker : 32A DP MCB
Cable: 4x1C-4mm2 NYY + 1x1c-4mm2 BYA as ECC
Sub Distribution Board-03
Serial No | Descripting of Items | Considered Rating(Watt) | Quantity | Total Wattage | D.F(%) | Maximum Demand(Watt)
i. | Lights
| Chandelier | 400 | 1 | 400 | 100% | 400
| Flat LED Light | 80 | 4 | 320 | 100% | 320
| Exhibition Spot Light | 15 | 3 | 45 | 60% | 27
| Mirror Light | 15 | 10 | 150 | 60% | 90
| Tube Light | 40 | 8 | 320 | 60% | 192
| Wall bracket light (WL) | 40 | 2 | 80 | 60% | 48
| Ceiling light (CL) | 40 | 23 | 920 | 60% | 552
| Door Light | 30 | 2 | 60 | 100% | 60
| Security Light | 50 | 1 | 50 | 100% | 50
| Garden Light | 40 | 3 | 120 | 60% | 72
ii | Power Sockets
| 5A-2pin | 300 | 2 | 600 | 50% | 300
| 13A-3pin | 1000 | 4 | 4000 | 50% | 2000
iii. | Others
| Washroom Exhaust Fan | 36 | 7 | 252 | 60% | 151.2
iv. | AC Loads
| Central AC | 3000 | 2 | 6000 | 100% | 6000
| AC(1.5 TON) | 1500 | 1 | 1500 | 100% | 1500
Total Maximum Demand | [5 empty] | 11762.2
|  |  |  | with 10% spare |  | 12938.42
|  | Therefore, I |  |  |  | 22.5
|  |  |  | with25% of RF |  | 28.125
Circuit Breaker : 32A DP MCB
Cable: 4x1C-4mm2 NYY + 1x1c-4mm2 BYA as ECC